[NOTE; ALL FIELDS MUST BE COMPLETED.

For items not applicable to the project, please insert “N/A”.]

| Project Name |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Interconnection Customer |  |  |  |  |  |  |  |
| Technical Contact Information | Name |  |  |  |  |  |  |
|  | Phone # |  |  |  |  |  |  |
|  | Email |  |  |  |  |  |  |
| Project Type/Size | Type: |  | <wind, biogas, solar, energy storage, etc.> |  |  | Size (MW): |  |
| Project Location (Address & Coordinates) |  |  |  |  |  |  |  |
| POI | <Point of Interconnection (POI): (include voltage, line name and number and/or station name, and coordinates in decimal degrees (DD))> |  |  |  |  |  |  |
| Initial Backfeed Date (IBD) |  | In-Service Data (ISD) |  |  | Commercial Operation Date (COD) |  |  |
| <Month/year> |  | <Month/year> |  |  | <Month/year> |  |  |

## CRITERIA

In addition to applicable industry standards and specifications, the Project and associated Interconnection Customer Attachment Facilities must adhere to, and comply with, National Grid’s technical specifications (i.e., Electric System Bulletins (“ESBs”), Transmission Planning Criteria TGP28 (“TGP28”)) and its environmental and real estate guidelines and requirements provided on the National Grid Wholesale Interconnection/New York website:

https://www.nationalgridus.com/Wholesale-Interconnections/New-York/

## DIAGRAMS/DRAWINGS

[NOTE: FOR EXISTING FACILITIES, CHANGES (I.E., REPLACEMENTS, ADDITIONS, ETC) SHALL BE CLOUDED ON THE DIAGRAM.]

  - Conceptual Operating Diagram

Provide current conceptual Operating Diagram (i.e., breaker level diagram, switching diagram) which must include: (i) Generating Facility, (ii) generator step up transformer (GSU), feeder(s) and their length(s), (iii) Interconnection Customer-owned Project Station (i.e., Collector Station, PSU Station), (iv) generator tie line(s) from the Project Station to POI(including approximate length), (v) the POI with approximate distances to terminal end stations (if applicable), (vi) the Point of Change of Ownership (PCO) (if known), (vii) metering points (if known), (viii) station service, and (ix) proposed reactive compensation devices. The diagram should include information like kV levels, circuit distances, transformer MVA ratings and impedances (Z and X/R), total plant MW, number of units per feeder, unit MW and MVA at power factor, unit type, etc.

☐  OPERATING/SWITCHING DIAGRAM INCLUDED

  - Conceptual Relay One Line/Single Line

Provide conceptual Relay One Line/Single Line for the Project Station (i.e., Collector Station, PSU Station).

☐  RELAY ONE LINE/SINGLE LINE INCLUDED

  - Preliminary Overall Project Site/Plot Plan

Provide preliminary Overall Project Site/Plot Plan which must include: (i) the Generation Facility, (ii)Project Station (i.e., Collector Station, PSU Station) with coordinates for the approximate expected location of the station, (iii) proposed POI with coordinates (in decimal degrees (DD)), (iv) anticipated location(s)/route(s) of the collection system feeders, and the (v) conceptual expected route of the generator tie line(s) between the PCO and POI.

☐  OVERALL PROJECT SITE/PLOT PLAN INCLUDED

  - Preliminary Overall Project Station Site/Plot Plan

Provide preliminary Project Station (i.e., Collector Station, PSU Station) Site/Plot Plan which must include: (i) the proposed layout of the Project Station in relation to the POI and transmission/distribution corridor(s), (ii) POI, (iii) coordinates for the approximate expected location of the Project Station, (iv) the anticipated location/route and length of the generator tie line between the Project Station and the PCO or POI.

☐  PROJECT STATION SITE/PLOT PLAN INCLUDED

  - POI Station Site Plan

If a new POI Station (e.g., ring bus station) is required for interconnection of the project (refer to TGP28), a preliminary site plan must be provided and must include: (i) the proposed orientation of the POI Station in relation to the Project Station and POI, (ii) the transmission/distribution corridor, (iii) the POI, and (iii) coordinates (in decimal degrees (DD)) for the approximate expected location of the proposed location of the POI Station.

☐  POI STATION PRELIMINARY SITE PLAN INCLUDED

## DATA

## Project Description

Provide a written description of the proposed project, including an element-by-element description of the one-line diagram, from generators, GSU, feeders, Project Station PSUs, lines, up to and including the POI and its relation (distances) with remote ends or existing substation (as the case may be).

[NOTE: FOR EXISTING FACILITIES, DESCRIBE BOTH EXISTING AND NEW.  IF EQUIPMENT IS BEING REPLACED, DESCRIBE THE EXISTING AND WHAT IT IS BEING REPLACED WITH.]

## Collection System Description

Provide written description of collection system, including number of feeders, units per feeder, etc.

(For multiple feeders, a table containing the length and impedances of each feeder must be included.)

## Generating Facility Data

### Type/Model/Manufacturer:

| Type | Model | Manufacturer |
| --- | --- | --- |

(Note: For wind turbines identify whether it is Type 3 or Type 4.)

### Rated power of each unit:

| MVA | MW @ power factor | Total Plant |
| --- | --- | --- |

### For energy storage supply:

| Energy storage capability (MWh) |  |
| --- | --- |
| Duration for full discharge (i.e., injection) (Hours) |  |
| Duration for full charge (i.e., withdrawal) (Hours) |  |
| Maximum withdrawal from the system (i.e., when charging) (MW) |  |
| Primary frequency response operating range for electric storage resource |  |
| Minimum State of Charge (%) |  |
| Maximum State of Charge (%) |  |

### Inverter Data

| Inverter Manufacturer | Model Name | Model Number | Model Version |
| --- | --- | --- | --- |

Provide cut sheets for each type of inverter.

☐  CUT SHEETS FOR EACH TYPE OF INVERTER INCLUDED

### Aspen Modelling Data

All Generators will be modeled using the appropriate type as described in ASPEN Oneliner V15.9.

Provide PSCAD models for each type of inverter.

☐  PSCAD MODEL FOR EACH TYPE OF INVERTER INCLUDED

- Converter- Interface Resource Model data for all solar, BESS and Type 4 Wind projects:

| Number of Units |  |
| --- | --- |
| Unit MVA Rating |  |
| Unit MW Generation (>=0) or consumption (<0) |  |
| Max current (in multiple of full load) When + seq V (pu) > Max current (pu) = Otherwise reduce current to (pu) |  |
| Slope of + seq dynamic reactive current injection characteristic |  |
| Slope of - seq dynamic reactive current injection characteristic |  |
| Resource shutdown When a phase voltage exceeds (pu) When a phase voltage drops below (pu) |  |

- Type 3 Wind Data for a Type 3 Wind Project:

| Number of Units |  |
| --- | --- |
| Unit MVA Rating |  |
| Unit rated MW |  |
| Unit MW generation |  |
| Converter current limits: |  |
| Rotor side limit (pu) |  |
| Grid side limit (pu) |  |
| Plant shutdown: |  |
| When a phase voltage exceeds (pu) |  |
| When a phase voltage drops below (pu) |  |
| Rotor R |  |
| Rotor Leakage L |  |
| Stator R |  |
| Stator Leakage L |  |
| Mutual L |  |
| Slip at rated kW |  |
| Filter X |  |

- Generator data for conventional project:

| Max design fault current contribution in per unit of full load current |  |
| --- | --- |
| X”/unit |  |
| X2/unit |  |
| X0/unit |  |

### Plant Station Load (MW)

| Summer | Winter |
| --- | --- |

### Proposed power factor capability range that can be achieved at the proposed maximum output (lagging-supply, leading-absorb) and corresponding Qmin and Qmax in MVAR (at the terminals)

| Qmin(absorb) | Qmax(supply) | Power factor |
| --- | --- | --- |

### Other proposed power factor/voltage compensation devices  (e.g., switched or fixed capacitors, SVCs, DVARs, etc.)

(Provide location, kV, type (static, dynamic), size (MVAR), nr. Steps, normal operation reaction time, during fault reaction time, etc. If there are none, then state as such.)

### Inverter Step-up Transformer

| Quantity |  | Type | ☐1ph |  | ☐3ph |
| --- | --- | --- | --- | --- | --- |
| Size (MVA) |  | Voltage (kV) |  |  |  |
| Nameplate self-cooled |  | Low(generator side) |  |  |  |
| 1st stage cooling |  | High (system side) |  |  |  |
| 2nd stage cooling |  | Tertiary |  |  |  |

| ☐Fixed Taps | ☐Non-LTC | ☐LTC | % range: |
| --- | --- | --- | --- |

| Winding Connections |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VLOW |  |  | VHIGH |  |  | VTERTIARY |  |  |
| ☐delta | ☐wye | ☐wye-grounded | ☐delta | ☐wye | ☐wye-grounded | ☐delta | ☐wye | ☐wye-grounded |

| Two Winding Transformer Impedance (in pu on self-cooled MVA rating) |  |  |  |
| --- | --- | --- | --- |
| Positive Sequence |  | Zero Sequence |  |
| Z1 | X/R | Z2 | X/R |

| Three Winding Transformer Impedance (in pu on self-cooled MVA rating) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Positive Sequence |  |  |  | Zero Sequence |  |  |  |
| Z1 (H-L) | Z1 (H-T) | Z1 (L-T) | X/R | Z0 (H-L) | Z0 (H-T) | Z0 (L-T) | X/R |

| Neutral Grounding Impedances (Ohms) |  |
| --- | --- |
| Reactor | Resistor |

### Plant Step-up Transformer

| Quantity |  | Type | ☐1ph |  | ☐3ph |
| --- | --- | --- | --- | --- | --- |
| Size (MVA) |  | Voltage (kV) |  |  |  |
| Nameplate self-cooled |  | Low(generator side) |  |  |  |
| 1st stage cooling |  | High (system side) |  |  |  |
| 2nd stage cooling |  | Tertiary |  |  |  |

| ☐Fixed Taps | ☐Non-LTC | ☐LTC | % range: |
| --- | --- | --- | --- |

| Winding Connections |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VLOW |  |  | VHIGH |  |  | VTERTIARY |  |  |
| ☐delta | ☐wye | ☐wye-grounded | ☒delta | ☐wye | ☐wye-grounded | ☒delta | ☐wye | ☐wye-grounded |

| Two Winding Transformer Impedance (in pu on self-cooled MVA rating) |  |  |  |
| --- | --- | --- | --- |
| Positive Sequence |  | Zero Sequence |  |
| Z1 | X/R | Z2 | X/R |

| Three Winding Transformer Impedance (in pu on self-cooled MVA rating) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Positive Sequence |  |  |  | Zero Sequence |  |  |  |
| Z1 (H-L) | Z1 (H-T) | Z1 (L-T) | X/R | Z0 (H-L) | Z0 (H-T) | Z0 (L-T) | X/R |

| Neutral Grounding Impedances (Ohms) |  |
| --- | --- |
| Reactor | Resistor |

### Line Reactor

| Voltage | Impedance |  |
| --- | --- | --- |
| (kV) | (mH) | Per Unit |

### Generator Lead Line (line between POI and Collector Station)

| Type |  |  | Cicuit Distance |
| --- | --- | --- | --- |
| ☐O/H | ☐U/G | ☐O/H&U/G |  |

| Impedances (pu on 100 MVA base, in components R and X) |  |
| --- | --- |
| Positive Sequence (Z1=R1+jX1) | Zero Sequence (Z0=R0+jX0) |

(NOTE: IF THE GENERATOR LEAD LINE IS COMPRISED OF BOTH UNDERGROUND AND OVERHEAD CONSTRUCTION, THEN THE LINE LENGTHS AND IMPEDANCES FOR EACH SECTION OF OVERHEAD AND UNDERGROUND ARE TO BE PROVIDED.)